## Audit Guidelines
CIVIL CONCRETING PROCESS GUIDELINES
QUALITY ASSURANCE & CONTROL COMPLIANCE
GUIDE LINES FOR PROJECT TEAM
AMPLIFICATION NOTES:
1 | This document is an attempt to guide the Project Managers & their teams towards the direction in which the Quality Assurance & Control is expected to be implemented in the Concreting and related works.
2 | The format of this Guidelines shall be used for recording the complainces by the project teams. These guidelines have been derived from the various process documents, industry standards & practices and work experience. The items in this document are by no means conclusive and limited - the project teams are expected to use their basic engineering knowledge, coupled with the various Standards/Codes related to the work at hand, to ensure that Quality, as expected from the project teams, is delivered, and recorded appropriately.
3 | The Project Managers are expected to prepare/generate this document as relevant to their Project SOW, and to visit this document regularly (as an Aide-de-Memoire) to ascertain themselves that the project is compliant to the QA/QC deliveries.
4 | The Project manager shall generate this document on the 30th of every month, to be kept on record, as an auditable document.
5 | This document shall be read in conjunction with the Audit Mandate and other operating checklists.
6 | The Project teams are expected to go through the relevant Manuals/Policy/Standards Documents and Codes and prepare the project specific questionnaire based on the guidelines given below, for recording of their compliance.
7 | In case a process/item is not applicable, it will be clearly mentioned so, with the appropriate reason (this will be verified through appropriate documents) - just a remark as 'NA' will not suffice.
8 | This document shall be produced for Audit, when called for.
Project Name: Kauvery Hospital | [5 empty] | Type of Project: Hospital Building
Location: Kovilambakkam, Chennai | [5 empty] | PjM Scope: Project Management
Project Manager: Project Lead: | [5 empty] | Stage of Audit: | Pre-Construction/Construction/Post Construction/Other
Date of Commencement: 17th Aug 2021 | [5 empty] | Date of Completion: 16th May 2022
Date (this document prepared on): 31st October 2021
S No. | ITEM | EXPLANATORY NOTES | COMPLIANCE |  |  | DETAILED OBSERVATIONS | TARGET DATE | REMARKS
|  |  | Y | N | NA
A | QUALITY STANDARDS/DOCUMENTS
1 | Are the following documents available at the Project Office/site?
a | PjM Process manuals & Documents
b | CBRE Agreement/SOW
c | Contractors' Contract Agreements
d | Standard Check lists/Pour cards for all Construction management Activities
e | Relevant IS/Building Codes for Reference(with PjM or Contractor or Client)
f
g
h
B | Objectives/Roles and Responsibilities (QA/QC)
1 | Has the PM set the Project QA/QC Objectives, w.r.t CBRE SOW and related industry standards/norms ?
2 | Are all team members aware of these Objectives?
3 | Is each team member aware of his/her objectives/Roles and responsibilities ?
4 | Are the same being monitored and reviewed as per policy?
5
C | PEP
1 | Was the Project initiation conducted ?
2 | Is the PDP prepared by the PM and scrutinized by the ROH?
3 | Does the PDP cover the QA/QC aspects listed here-in, as required by the SOW?
4 | Has this been included as part of the PEP?
5 | Has the same been shared with the Client, and his feedback/approval taken?
6 | If there are deviations from PjM QC Process, have the same been conveyed to the RH/ROH and clarity sought on the way ahead?
7 | Is the Project specific QA/QC for civil works, duly approved by Consultants, available with PjM ?
8
9
D | Concrete Mix design
1 | Has the Consultant/RMC vendor submitted the mix design? |  | Yes |  |  | RMC vendor submitted and same approved by consultant through mail date: 19th Sep 2021
2 | Was the design mix tested (cube test) and results accepted? |  | Yes
3 | Has the mix design been verified/ratified through an approved agency/third party? |  |  | No
4 | Has the consultant issued the final approved mix design to be used for the construction? |  | Yes
5 | Has the mix design been forwarded to the concrete supplier for compliance? |  |  | No
6
E | Construction Material & Concrete supply.
1 | Are the Consultant approved technical specifications, w.r.t all construction material and/or RMC available ? |  | Yes
2 | Do all the construction materials like Cement, sand, aggregate, ad-mixtures etc. meet the laid down tech specifications? | Test Reports and sample approvals of respective materials as supporting documents | Yes |  |  | Client confirmed that the site test & third party test not required
3 | Is the sample approval Register being maintained at site and up to date? |  |  | No
4 | Is the calibration certificate for the Batching plant supplying concrete, available? |  | Yes
5 | Has the initial batch been verified for its compliance with the Design mix? | Verification through the data available on the batching slips. Verification of cubes through a third party testing. | Yes
6 | Is the data w.r.t Project Name and the mix design details fed correctly, into the batching Plant? |  | Yes
7 | Are copies of the batching slip maintained by PjM? |  | Yes
8 | Are the batching slips legible? |  | Yes
9 | Are the batching slips being randomly verified for compliance with the Design Mix? | Verification through the data available on the batching slips. Verification of cubes through a third party testing. | Yes
10 | Is the record of despatch, arrival, and pour details w.r.t transit mixers being maintained? | Batching slips and despatch details. | Yes
11 | Are delivery challans for Client supplied materials maintained on record? | If the delivery challans, as a practice, are being maintained by the Contractor, copies of random challans (especially those which have been used to verify design mix and other data) must be held on record with PMC. |  |  | NA
12
F | Pour Activities
1 | Are pour cards generated for every pour? |  | Yes
2 | Do the pour cards have both pre-pour and post pour checklists? | Post pour checklists to include post pour inspection, curing, deshuttering and final inspection stages also. | Yes
3 | Are all the the pour cards complete in all respect, duly attested by all concerned (including Safety officers)? |  | Yes
4 | Do the pour cards reflect the stage wise clearances to the Contractor to proceed with the concreting cycle? | Ideally, next stage of a concreting cycle should not commence unless all observations of the previous stage are closed. | Yes
5 | Do the pour cards reflect the design grade of concrete being used in that pour? |  | Yes
6 | Are the observations (if any) on the finished surface, post de-shuttering, recorded in the Pour card? | E.g. honey-combing, exposed re-bars, sagging, bulging, cracks etc. | Yes
7 | Have these observations been rectified and closure recorded in the Pour Card? |  | Yes
8 | Is curing record maintained and updated by Contractor? |  | Yes
G | Water Proofing Works
1 | Has the Waterproofing method statement been submitted by the Vendor?
2 | Has the same been vetted by CBRE and forwarded to the consultant for approval?
3 | Has the Waterproofing Checklist been downloaded from CR or derived from the Method statement? | Either the Checklist can be downloaded from the CR, or derived from the Method statement (as applicable depending on the type of Waterproofing treatment being done).
4 | Has this checklist been forwarded to the Contractor(s) for use?
5 | Are the Waterproofing works being executed as per the checklists?
6 | Are the following being checked/implemented :-
a | Approval and certification of the applicator by the manufacturer of the barrier system
b | Provision in the design for subsurface and surface drainage systems to reduce water pressure (where this is applicable)
c | Continuous support provided for sheet barriers during handling so that punctures do not occur
d | Protection provided for the barrier when work is performed over it or near it
e | Protection provided for the membrane system before backfilling
f | On horizontal installations, flood tests performed after work is completed
g | Guarantee received from the manufacturer, with whatever limitations are necessary regarding its performance
H | Structural Steel Works
1 | Are the consultant approved (shop) drawings and concerned tech specifications for the structural steel members available?
2 | Are copies of material test reports for structural steel maintained by PjM
3 | Are the checklists for erection of structural steel correctly filled up and endorsed by all concerned? | Method statement from contractor will help in generating Checklist
4 | Are the checklists for welding works filled up correctly and endorsed by all concerned?
5
6
J | Miscellaneous Works
1 | Are checklists for lintel works available? | Method statement from contractor will help in generating Checklist | Yes
2 | Are the lintel works being executed as per checklists? |  |  |  | NA | Work not yet started
3 | Are checklists for RW works available? |  | Yes
4 | Are the RW works being executed as per checklists? |  | Yes
5 | Are checklists for Water/RCC tank works available? |  |  | No
6 | Are the Water/RCC tank works being executed as per checklists? |  |  |  | NA | Work not yet started
7 | Is the scaffolding erected as per design certified by an approved authority? |  |  | No
8 | Has the scaffolding structural stability certificate been obtained from the concerned Contractor? | Undertaking letter given by civil vendor | Yes |  |  | Undertaking letter submitted by M/s plaza Properties
K | Testing of Concrete and other materials
1 | Is the slump register maintained at site and up-to-date? |  | Yes
2 | Apart from other details, does the slump register have the batching slip details, area of concreting and time of slump test condcuted ? |  | Yes
3 | Are the batches failing slump test rejected and segregated? |  |  |  | NA
4 | Is the Cube register maintained at site and up-to-date? |  | Yes
5 | Are the cubes correctly linked to the area of pours, in the Cube register? |  | Yes
6 | Apart from other details, does the cube register show 3, 7 and 28 days results and references to Consultant approval / rejection in case the results are not ok? |  | Yes |  |  | 7&28 days result and shared to consultant for review. Mail shared to consultant in weekly basis
7 | Are the cubes being cast and tested as per the standard codes/contract? |  |  | No |  | As per the client instruction cube casting done
8 | Are results related to failed cubes refered to the Consultant and his advice/feedback recorded for further action? |  | Yes |  |  | Failed cube result shared to consultalt on 29-10-21 through mail and reply from consultant, to do the Non Distractive hammer test, Based on this result , will give the further solution. Please stop , this company RMC for further work. same was informed to M/s plaza properties.
9 | Is third party test being conducted for cubes? |  | Yes |  |  | All the 7days & 28days cube strength was conducted in third party lab Falcon testing lab, perugudi, Chennai. Advised by M/s kauvery
10 | Are all the testing equipment etablished in the site labs, caliberated as per standard periodicity/at least once in 06 months? |  |  |  | NA | No site lab
11 | Is a copy of calibration certificates maintained by PjM ? |  |  |  | NA | No site lab
12 | Are copies of test reports for re-bars maintained by PjM |  | Yes |  |  | Site test like unit weight, bend & rebend test. And MTC by supplier was maintained
13 | Are copies of the test reports for Client supplied materials maintained by PjM? |  |  |  | NA
14 | Are the Client supplied materials being reconciled through reconciliation statements as required? |  |  |  | NA
15 | Water for Construction:-
a | Have approved source(s) of water been listed/identified? |  |  |  | NA | Bore well water used for construction purpose, located in north side of building
b | Is the water being supplied from the approved source(s)? |  |  |  | NA
c | Have initial samples of the water being supplied, tested for the required/laid down standards for use of the water in construction activities? | Bore well water | Yes |  |  | Eco Lab valid upto 4th Jan 22
d | Does the test report satisfy the above required/laid down standards? |  | Yes |  |  | report received on 05-10-21 through mail
e | Has the water been tested in the last quarter? |  |  |  | NA | To be done next test on 1st Jan '22
f | Does the test report satisfy the required/laid down standards for use of the water in construction activities? |  | Yes
L | Consultant/TP feedback
1 | Are the observations from Consultants/Clients/TP etc recorded? | This is to be obtained as part of their visit feedback and recorded in a register/maintained as a folder (in case of mail/MoMs)
2 | Has the feedback/compliance to such observations been forwarded to all concerned?
3 | Are corrective and preventive actions taken and recorded?
4
M | Records to be maintained
By PjM:-
1 | Original List (duly signed by Contractor and PjM) of quality related original records under Contractor's custody. |  |  | No
2 | Approved Project Specific QA/QC manual - Original |  |  | No
3 | Original Pour Cards | Once the particular concreting is over, the originals to be held with PjM. | Yes |  |  | Power app checklist followed
4 | Copy of batching slips |  | Yes |  |  | Photo copy have. Orginal submitted to M/s Kauvery
5 | Copy of Material Test certificates |  |  | No |  | No site test/ 3rd party test conducted for materials
6 | Copy of site lab calibration certificates |  |  |  | NA | No site lab
7 | Copy of batching plant calibration certificates |  | Yes |  |  | Ramco submitted through Mail
8 | Copy of Checklists for structural steel works |  |  | No
9 | Copy of checklists for misc works like lintels etc. |  |  |  | NA
10 | Quality related site notes |  | Yes |  |  | Power app checklist followed
11 | Consultants/Client inspection/comments/approvals |  |  | No
12 | Any other records/documents (or their copies) that may be required, in keeping with the SOW, best practices and codal standards. |  |  | No
13 | Copy of Slump Register | Copies of relevant pages/extracts from these registers to be kept at PjM, where ever and when ever it is felt essential/required. | Yes
14 | Copy of Cube Test register |  | Yes
15 | Copy of Curing register |  | Yes
16 | Sample Approval Register |  |  | No
17 | CAP register |  |  | No
By Contractors:-
1 | Copy of Approved Project Specific QA/QC manual - Original |  |  | No
2 | Copy of List (duly signed by Contractor and PjM) of quality related original records under Contractor's custody. |  |  | No
3 | Cement register(in case of client supply) |  | Yes |  |  | To be updated
4 | Steel register |  | Yes |  |  | To be updated
5 | Original Pour Cards signed by PjM | To be maintained by the Contractor till the pour cycle is in progress, and subsequently to be handed over to PjM for custody. Contractor may keep a copy. |  | No
6 | Original of batching slips signed by PjM |  | Yes |  |  | yes same was submitted to client during RA bill
7 | Original Slump register |  | Yes
8 | Original Curing register |  | Yes
9 | Original Cube test register-updated and signed by PjM |  | Yes
10 | Original of Material Test certificates |  |  | No |  |  |  | MTC avaliable
11 | Original of site lab calibration certificates |  |  |  | NA |  |  | No lab at site
12 | Original of batching plant calibration certificates |  |  | No |  |  |  | In Mail copy
13
14
|  | Area/Package Incharge | PM/CM |  |  | Account Lead/PL
SIGNATURE:
NAME:
DATE:
FOR VERIFICATION BY THE PROJECT MANAGER/PROJECT LEAD:
N | Status of previous/pending NCs & Observations on QA/QC | These NCs could be from any or all sources, e.g. External Audits, Internal Audits, Client visit/observations, consultant obsertvations etc.
1 | Are all previous NCs addressed and closed? |  |  | No
2 | If not, list the open/pending NCs below and give its current status:-
| NC ITEM/DETAILS | STATUS (OPEN/CLOSE) WITH REASON | TARGET DATE |  |  | REMARKS
a | This is to inform that sagging of slab is observed at commercial staircase closing at 1st floor. Kindly rectify the same | Open - Slab de-shuttering to be done | 2021-11-05
b
c
d
e
|  | PM/CM | Account Lead/PL
SIGNATURE:
NAME:
DATE:
Format No. B020-L3-Cvl-G-008/Rev01/Jul2015

## Checklist
Checklist for Quality Aduit
PACIFICA TECH PARK
Package |  |  |  | Inspection Report No
Vendor |  |  |  | Date/Time
|  |  |  | Inspected by |  | Name
Description of Work | [5 empty] | Signature
Wing |  | Dwg Ref.No |  | Rev
Floor |  |  |  | Inspection Request No
Location |  |  |  | Date
S. No | Description |  |  | Yes | No | Remarks
1 | Is the latest revision of drawing available?
2 | Is the checklist followed?
3 | Is the QC Engineer/Supervisor avaliable at site?
4 | Is the material inspection report followed at site?
5 | Is the material MTC/ Third party test certificate avaliable at site?
6 | Is the Quality Site Note/NCR tracker avaliable at site?
7 | Is the Curing register avaliable at site?
8 | Approved QAQC manual avaliable at site?
9 | Work methodology avaliable at site?
10 | Approved Sample approval display/ Register avaliable at site?
11
Observations if any :
Contractor/Vendor |  |  | CBRE |  |  | Client
Signature : |  |  | Signature : |  |  | Signature :
Name : |  |  | Name : |  |  | Name :
Date : |  |  | Date : |  |  | Date :
Legend: NA - Not Applicable